## criticality
Original Sort | Source | Duplicate Equipment | EQUIPMENT | ASSET_ID | EQUIPMENT_DESCRIPTION | PROC_CODE | P_FAM | P_Mod | JDE_Crit | EQ_Stat | Project | PROD BU Review | CO | SC | BAR | SIF | BMS | HAZ | VOLT | GAS | EEHA | MECH | ELECT | ENV | H&S Lik. | H&S Cons. | H&S Crit. Asses. | H&S Crit. Rules. | H&S Crit. Final Num. | ENV Lik. | ENV Cons. | ENV Crit. Asses. | ENV Crit. Rules. | ENV Crit. Final Num. | CO Lik. | CO Cons. | CO Crit. Asses. | CO Crit. Rules. | CO Crit. Final Num. | PROD Lik. | PROD Cons. | PROD Crit. Asses. | PROD Crit. Rules. | PROD Crit. Final Num. | Highest Crit. | Overall ABC | JDE Crit Equiv. | Comments | Plant | Grouping
28123 | JDE Data 20251105 | FALSE | 1346RO0401 | 148692 | Flow Orifice T0364 Overflow #1 | UAN | VRE | MVAR |  | DF | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28124 | JDE Data 20251105 | FALSE | 1346RO0402 | 148693 | Flow Orifice T0364 Overflow #2 | UAN | VRE | MVAR |  | DF | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28125 | JDE Data 20251105 | FALSE | 1346RO0403 | 148694 | Flow Orifice T0364 Overflow #3 | UAN | VRE | MVAR |  | DF | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28128 | JDE Data 20251105 | FALSE | 1346RO0404 | 148697 | Flow Orifice T0365 Overflow #1 | UAN | VRE | MVAR |  | DF | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28130 | JDE Data 20251105 | FALSE | 1346RO0405 | 148699 | Flow Orifice T0365 Overflow #2 | UAN | VRE | MVAR |  | DF | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28132 | JDE Data 20251105 | FALSE | 1346RO0406 | 148701 | Flow Orifice T0365 Overflow #3 | UAN | VRE | MVAR |  | DF | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28134 | JDE Data 20251105 | FALSE | 1346RO0407 | 148704 | Flow Orifice T0366 Overflow #1 | UAN | VRE | MVAR |  | DF | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28135 | JDE Data 20251105 | FALSE | 1346RO0408 | 148705 | Flow Orifice T0365 Overflow #2 | UAN | VRE | MVAR |  | DF | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28181 | JDE Data 20251105 | FALSE | 1346T0364 | 148764 | Tank UAN Flexitank Storage #1 | UAN | TNK | CBDS | LOW | FU | Geraldton Liquid Ferts | 3 Reviewed by BU | [27 empty] | E | 3 | 1 L | 1 L | 1 | 1 L | E | LOW | Failure of bladder - causing delays (very unlikely) Have redundancy and can continue loading if no damage or risk | Geraldton - Liquid Fert | FERTS - Regional
28200 | JDE Data 20251105 | FALSE | 1346T0365 | 148783 | Tank UAN Flexitank Storage #2 | UAN | TNK | CBDS | LOW | FU | Geraldton Liquid Ferts | 3 Reviewed by BU | [27 empty] | E | 3 | 1 L | 1 L | 1 | 1 L | E | LOW | Failure of bladder - causing delays (very unlikely) Have redundancy and can continue loading if no damage or risk | Geraldton - Liquid Fert | FERTS - Regional
28203 | JDE Data 20251105 | FALSE | 1346T0366 | 148786 | Tank UAN Flexitank Storage #3 | UAN | TNK | CBDS | LOW | FU | Geraldton Liquid Ferts | 3 Reviewed by BU | [27 empty] | E | 3 | 1 L | 1 L | 1 | 1 L | E | LOW | Failure of bladder - causing delays (very unlikely) Have redundancy and can continue loading if no damage or risk | Geraldton - Liquid Fert | FERTS - Regional
28205 | JDE Data 20251105 | FALSE | 1346T0367 | 148788 | Tank UAN Flexitank Storage #4 | UAN | TNK | CBDS | LOW | FU | Geraldton Liquid Ferts | 3 Reviewed by BU | [27 empty] | E | 3 | 1 L | 1 L | 1 | 1 L | E | LOW | Failure of bladder - causing delays (very unlikely) Have redundancy and can continue loading if no damage or risk | Geraldton - Liquid Fert | FERTS - Regional
28234 | JDE Data 20251105 | FALSE | 1346W0241 | 148818 | Valve Isolation UAN U/S Of Bund Wall | UAN | VMA | MVAM | NOT | FU | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28235 | JDE Data 20251105 | FALSE | 1346W0242 | 148819 | Valve Drain UAN U/S Of Bund Wall | UAN | VMA | MVAM | NOT | FU | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28238 | JDE Data 20251105 | FALSE | 1346W0401 | 148822 | Valve Isolation UAN Supply To Flexitanks | UAN | VMA | MVAM | MED | AV | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28239 | JDE Data 20251105 | FALSE | 1346W0402 | 148823 | Valve Drain UAN Flexitank Supply Line | UAN | VMA | MVAM | MED | AV | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28240 | JDE Data 20251105 | FALSE | 1346W0403 | 148824 | Issued - Not used | UAN | VMA | MVAM | MED | FU | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28241 | JDE Data 20251105 | FALSE | 1346W0404 | 148825 | Valve Isolation UAN Supply To Flexitank #1 Manfld End | UAN | VMA | MVAM | MED | AV | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28242 | JDE Data 20251105 | FALSE | 1346W0405 | 148826 | Valve Isolation UAN Supply To Flexitank #1 Tank End | UAN | VMA | MVAM | MED | AV | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28243 | JDE Data 20251105 | FALSE | 1346W0406 | 148827 | Valve Isolation UAN Supply To Flexitank #2 Manfld End | UAN | VMA | MVAM | MED | AV | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
28244 | JDE Data 20251105 | FALSE | 1346W0407 | 148828 | Valve Isolation UAN Supply To Flexitank #2 Tank End | UAN | VMA | MVAM | MED | AV | Geraldton Liquid Ferts | 2 Assessed by Consultant | [27 empty] | D | 1 | 1 L | 1 L | 1 | 1 L | E | LOW |  | Geraldton - Liquid Fert | FERTS - Regional
Note on AQ1: Lee Fitzmaurice: =VLOOKUP([@[PROD Lik.]]&[@[PROD Cons.]],Table1[[Concat]:[Outcome]],2,FALSE)
Note on AR1: Lee Fitzmaurice: =IF(LEFT([@[PROD BU Review]],1)="9","0 N",[@[PROD Crit. Asses.]])
Note on AX1: Lee Fitzmaurice: =IFERROR(VLOOKUP(LEFT([@EQUIPMENT],4),Table11,2,FALSE),"???")
Note on AY1: Lee Fitzmaurice: =IFERROR(VLOOKUP(LEFT([@EQUIPMENT],4),Table11,3,FALSE),"???")

## Criticality Matrix
Criticality Matrix |  |  | Environ
Safety
Compliance
|  |  | Production | 0-12hr loss | 12-24hr loss | 1-3day loss | 3-5day loss | 5+ day loss
| Likelihood |  |  | 1 | 2 | 3 | 4 | 5
|  | Many times per year | A | Moderate | Moderate | High | Extreme | Extreme
|  | 1 per year | B | Low | Moderate | High | Extreme | Extreme
|  | 1 per 5 yr | C | Low | Moderate | High | High | Extreme
|  | 1 per 10 yr | D | Low | Low | Moderate | High | High
|  | 1 per 30 yr | E | Low | Low | Low | Moderate | High

## hierarchy
Equipment Number | Desscription | Asset Class | Object Type | Parent Asset | Discipline | Asset Make | Asset Model | Asset Department | Safety Critical Code | Compliance Code | Environmental Code | EEHA Code | Asset Criticality ABC | Long Text | Location | Cost Centre | Work Centre | planner group | Process Code
1150P0052 | Pump Cooling water | PMP | MPMC | AMM | Electrical | SULZER | 2435132 | Ammonia | [8 empty] | MECH02 | M02 | Water
1150MP0052 | Motor cooling water pump | MOT | EMOT | 1150P0052 | Electrical | WEG | 1234 | Ammonia | SC | CO | ENV | EEHA | B | long text description | AAN Block 1 Level 2 | 124131 | ELEC01 | E01 | Elec

## FMEA
Equipment | Subclass / Type | Variant | Components | Operating Context | Function | Functional Failure | Failure Mode | Failure Mechanism | Failure Cause | Failure Effect | Detectable under normal conditions? Or Hidden? | Column1 | Consequence Type | Consequence [1..5] | Likelihood [1..5] | Detectability [1..5] | RPN [/75] | Task Description | Task Acceptable Conditions | Corrective Action | Maintenance Activity Type | Task List ID | Interval | Units | Trade | Manning | Duration Hr | Location Photo | Documents | Safety / Hazards / PPE | Resources / Tools / Special Equipment
Control Valve |  |  | Valve Body | Exposed, close to the ocean (<500m) | To contain the process fluid and provide the main flow path through the valve. | Loss of ability to contain pressure or maintain a sealed flow path | External leakage | •Corossion | Salt-laden atmosphere, poor coating, material degradation | Environemental contamination, safety hazard | Detectable |  | Safety |  |  |  | 0 | External visual inspection of control valve body for signs of leakage, corrosion, or surface degradation | Valve body free from visible leakage, corrosion, or damage. Coating intact with no blistering or peeling. No cracks or deformation. | Raise a Work Request for repairs
Control Valve |  |  | Valve Body | Exposed, close to the ocean (<500m) | To contain the process fluid and provide the main flow path through the valve. | Loss of ability to contain pressure or maintain a sealed flow path | Body rupture | •Thermal stress •Stress Cracking | Overpressure, thermal cycling, casting flaw | Sudden loss of containtment, safety hazard | Detectable |  | Safety |  |  |  | 0 | External visual inspection of valve body for signs of cracks, deformation, or impact damage | Valve body structurally sound with no visible cracks, deformation, or impact damage. Welds intact. No signs of stress or strain. | Raise a Work Request for repairs
Control Valve |  |  | Valve Body | Exposed, close to the ocean (<500m) | To contain the process fluid and provide the main flow path through the valve. | Loss of ability to contain pressure or maintain a sealed flow path | Loss of pressure-retaining capability | •Erosion •Material thinning | High-velocity or abrasive media | Inability to maintain system pressure | Detectable with Anciliary Equipment | [5 empty] | 0 | Internal visual inspection for erosion, pitting, or thinning on high-velocity or abrasive flow surfaces. | Valve body free from erosion or wall thinning. No signs of internal wear, pitting, or material loss. Pressure boundary intact.
Control Valve |  |  | Valve Body | Exposed, close to the ocean (<500m) | To contain the process fluid and provide the main flow path through the valve. | Loss of ability to contain pressure or maintain a sealed flow path | Internal surface wear | •Erosion or cavitation | Poor flow control design, flashing | Reduced flow control accuracy | Hidden | [5 empty] | 0 | Internal visual inspection for erosion, or cavitation damage. | Internal surfaces of valve body free from erosion, cavitation damage, or material loss. No signs of pitting, gouging, or flow path deformation.
Control Valve |  |  | Valve Body | Exposed, close to the ocean (<500m) | To contain the process fluid and provide the main flow path through the valve. | Loss of ability to contain pressure or maintain a sealed flow path | Crack development | •Mechanical fatigue | Vibration, external impact, cyclic stress | Compomise structural intergirty | Hidden | [6 empty] | Internal & external close/detail visual inspection for cracks and damages. | Internal and external surfaces of valve body free from cracks. No signs of external damages
Control Valve |  |  | Trim (Plug/Disc, Seat, Stem, Cage/Guide) | Exposed to the process medium | To regulate and shut off process fluid flow within the valve. | Loss of ability to accurately control or shut off flow. | Leakage past seat | •Plug/seat wear •Deformation | Erosion, flashing, improper seating | Inability to shut off flow, bypass leakage | Detectable with Anciliary Equipment |  | Safety |  |  |  |  | Perform valve calibration using smart positioner to evaluate stroke response and shutoff behavior | Valve achieves full shutoff position with smooth, consistent travel and no indication of overtravel, drift, or sealing deviation during calibration. | Raise a Work Request for repairs
Control Valve |  |  | Trim (Plug/Disc, Seat, Stem, Cage/Guide) | Exposed to the process medium | To regulate and shut off process fluid flow within the valve. | Loss of ability to accurately control or shut off flow. | Sticking/jamming | •Galling •Corrosion •Debris lodging | Infrequent operation, poor air quality, misalignment, guide damage | No or slow valve response, fails to open/close properly | Detectable | [6 empty] | Review valve stroke signature online or perform partial stroke test | Valve stroke smooth and consistent with no signs of hesitation, sticking, or abnormal response. Valve position tracks control signal accurately during partial stroke or signature review. | Raise a Work Request for repairs
Control Valve |  |  | Trim (Plug/Disc, Seat, Stem, Cage/Guide) | Exposed to the process medium | To regulate and shut off process fluid flow within the valve. | Loss of ability to accurately control or shut off flow. | Stem misalignment or bending | •Mechanical stress •Improper support | Side-loading by actuator, over-travel, assembly misalignment | Plug mis-seats, poor control, mechanical wear in packing | Detectable | [6 empty] | Review valve stroke signature online or perform partial stroke test | Valve stroke is smooth and consistent with no irregularities. Stem is straight and properly aligned with the actuator. No signs of binding, offset movement, or side loading during testing or inspection. | Raise a Work Request for repairs
Control Valve |  |  | Trim (Plug/Disc, Seat, Stem, Cage/Guide) | Exposed to the process medium | To regulate and shut off process fluid flow within the valve. | Loss of ability to accurately control or shut off flow. | Seat damage or deformation | •Impact •Thermal distortion | Water hammer, hard shutoff, temperature cycling | Flow leakage under shutoff, chattering or unstable behavior | Hidden | [6 empty] | During valve overhaul inspect for impact damage, thermal distortion, or wear, and replace if sealing integrity is compromised. | Seat free from impact damage, deformation, or distortion. Seating surface smooth and capable of achieving proper shutoff. No cracks, warping, or irregular wear. | Raise a Work Request for repairs
Control Valve |  |  | Trim (Plug/Disc, Seat, Stem, Cage/Guide) | Exposed to the process medium | To regulate and shut off process fluid flow within the valve. | Loss of ability to accurately control or shut off flow. | Guide wear or damage | •Mechanical abrasion •Distortion | Misaligned stem, plug side-load, poor surface finish | Plug instability, sticking, excessive wear | Hidden | [5 empty] | 0 | During valve overhaul inspect for wear, scoring, or distortion, and ensure smooth plug movement without obstruction. | Guide surface smooth, undamaged, and properly aligned; plug moves freely without resistance or binding. | Raise a Work Request for repairs
Control Valve |  |  | Valve Bonnet (Gasket, Flange) | Exposed, close to the ocean (<500m) & exposed to process medium | To seal the valve body and support internal components. | Loss of sealing or pressure-retaining capability. | External leakage (gasket) | •Gasket degradation | Age degradation, overcompression, improper torque, corrosion | Process fluid leaks externally | Detectable |  | Safety |  |  |  | 0 | Perform visual inspection of bonnet flange area for signs of gasket degradation, including leakage, staining, or gasket extrusion. | No visible leakage, staining, or gasket extrusion; flange and gasket area clean, dry, and intact. | Raise a Work Request for repairs
Control Valve |  |  | Valve Bonnet (Gasket, Flange) | Exposed, close to the ocean (<500m) & exposed to process medium | To seal the valve body and support internal components. | Loss of sealing or pressure-retaining capability. | Bonnet bolt loosening | •Vibration •Relaxation | Improper tightening, cyclic loads, corrosion | Gasket compression loss, eventual leakage | Detectable | [5 empty] | 0 | Check bonnet bolts during inspection or overhaul for tightness and signs of loosening, corrosion, or uneven torque; re-torque as required | All bonnet bolts secure, evenly torqued, and free from corrosion or damage; no signs of looseness or preload loss. | Raise a Work Request for repairs
Control Valve |  |  | Valve Bonnet (Gasket, Flange) | Exposed, close to the ocean (<500m) & exposed to process medium | To seal the valve body and support internal components. | Loss of sealing or pressure-retaining capability. | Gasket extrusion/blowout | •Overpressure •Misalignment | Incorrect gasket selection, poor assembly, pressure surge | Sudden loss of containment, safety risk | Detectable |  | Safety |  |  |  | 0 | Perform visual inspection of bonnet flange area for signs of gasket gasket extrusion. | No signs of gasket extrusion, displacement, or deformation; bonnet flange area clean, dry, and intact. | Raise a Work Request for repairs
Control Valve |  |  | Valve Bonnet (Gasket, Flange) | Exposed, close to the ocean (<500m) & exposed to process medium | To seal the valve body and support internal components. | Loss of sealing or pressure-retaining capability. | Flange surface corrosion | •Corrosion | Salt-laden air, gasket leakage, poor material/coating | Loss of sealing integrity | Detectable | [5 empty] | 0 | Perform visual inspection of bonnet flange surfaces for signs of corrosion, pitting, or material degradation | Flange surfaces clean, free from corrosion, pitting, or damage; sealing surfaces intact and suitable for gasket contact. | Raise a Work Request for repairs
Control Valve |  |  | Packing System (Follower, Stud, Packing) | Exposed to the process medium & partial exposure to environment | To prevent process fluid from leaking along the valve stem. | Loss of sealing around the stem. | External leakage (stem) | •Packing wear •Hardening •Extrusion | Thermal cycling, over-tightening, age, abrasive media | Visible fluid leak along stem | Detectable | [5 empty] | 0 | Inspect packing area for signs of stem leakage, packing wear, hardening, or extrusion; adjust or replace packing as necessary | No visible leakage at packing; packing is intact, seated properly, and free from hardening, wear, or extrusion | Raise a Work Request for repairs
Control Valve |  |  | Packing System (Follower, Stud, Packing) | Exposed to the process medium & partial exposure to environment | To prevent process fluid from leaking along the valve stem. | Loss of sealing around the stem. | Packing blowout | •Packing ejection under pressure | Improper installation, missing follower/stud, sudden pressure rise | Sudden uncontrolled leak, safety risk | Detectable | [5 empty] | 0 | Inspect packing follower, studs, and gland for correct installation and tightness; ensure packing is properly seated to prevent ejection under pressure | Packing securely retained with follower and studs in place; no signs of displacement, looseness, or improper compression. | Raise a Work Request for repairs
Control Valve |  |  | Packing System (Follower, Stud, Packing) | Exposed to the process medium & partial exposure to environment | To prevent process fluid from leaking along the valve stem. | Loss of sealing around the stem. | Follower/stud loosening | •Loss of compression | Vibration, thermal expansion, improper torque, improper installation | Reduced packing preload, progressive leakage | Detectable | [5 empty] | 0 | Inspect packing follower, studs, and gland for correct installation and tightness; ensure packing is properly seated to prevent ejection under pressure | Packing securely retained with follower and studs in place; no signs of displacement, looseness, or improper compression. | Raise a Work Request for repairs
Control Valve |  |  | Packing System (Follower, Stud, Packing) | Exposed to the process medium & partial exposure to environment | To prevent process fluid from leaking along the valve stem. | Loss of sealing around the stem. | Packing galling on stem | •Adhesive wear on stem | Incompatible materials, dry contact, poor lubrication | Stem scoring, leakage, stem sticking | Hidden | [5 empty] | 0 | During valve overhaul, inspect stem and packing contact surfaces for galling or adhesive wear; clean, polish, or replace as required. | Stem surface smooth and free from galling, scoring, or adhesive wear; packing interface undamaged and suitable for proper sealing. | Raise a Work Request for repairs
Control Valve |  |  | Yoke | Exposed, close to the ocean (<500m) | To support and align the actuator and stem with the valve body. | Loss of structural support or misalignment. | Cracking or fracture | •Fatigue •Mechanical overload | Vibration, over-tightening, casting defect | Misalignment, actuator instability, structural failure | Hidden | [5 empty] | 0 | External close/detail visual inspection for cracks and damages | Yoke surface free from cracks. No signs of external damages
Control Valve |  |  | Yoke | Exposed, close to the ocean (<500m) | To support and align the actuator and stem with the valve body. | Loss of structural support or misalignment. | Corrosion | •Surface degradation | Salt-laden air, poor coating, galvanic corrosion | Loss of strength, bolt seizure, structural integrity risk | Detectable | [5 empty] | 0 | Perform visual inspection of yoke surfaces for signs of corrosion, pitting, or material degradation | Yoke surfaces clean, free from corrosion, pitting, or damage. | Raise a Work Request for repairs
Control Valve |  |  | Actuator Body | Exposed, close to the ocean (<500m) | To house and protect the internal components of the actuator. | Loss of integrity or inability to contain/control actuation pressure. | Corrosion - External | •Surface degradation | Moisture, salt-laden air | Housing weakening, air leakage, mounting failure | Detectable | [5 empty] | 0 | Perform visual inspection of actuator surfaces for signs of corrosion, pitting, or material degradation | Actuator surfaces clean, free from corrosion, pitting, or damage. | Raise a Work Request for repairs
Control Valve |  |  | Actuator Body | Exposed, close to the ocean (<500m) | To house and protect the internal components of the actuator. | Loss of integrity or inability to contain/control actuation pressure. | Corrosion - Internal | •Surface degradation | Contaminated instrument air | Housing weakening, air leakage, mounting failure | Hidden | [5 empty] | 0 | During valve overhaul, inspect actuator interior for corrosion, moisture ingress, or internal surface degradation | Actuator interior clean and dry, with no corrosion, pitting, or material degradation. Internal components intact and functional. | Raise a Work Request for repairs
Control Valve |  |  | Actuator Body | Exposed, close to the ocean (<500m) | To house and protect the internal components of the actuator. | Loss of integrity or inability to contain/control actuation pressure. | Seal leakage (cover joints) | •Gasket •O-ring degradation | Aging, improper installation | Air leak, pressure loss, inconsistent valve response | Detectable | [5 empty] | 0 | Inspect actuator area for signs of gasket or O-ring degradation, hardening, or damage | Seals intact and properly seated with no cracks, hardening, or deformation; cover joints dry and leak-free. | Raise a Work Request for repairs
Control Valve |  | Diaphragm | Diaphragm/ Piston | Exposed to the quality of internal instrument air | To convert air pressure into linear or rotary motion. | Loss of ability to transmit force or respond to control pressure | Rupture or tearing | •Fatigue •Stress •Material defect | Aging, excessive pressure, chemical attack, poor air quality | Loss of motion, actuator fails to stroke | Detectable | [5 empty] | 0 | Review valve stroke signature online or perform partial stroke test | Valve stroke is smooth and consistent with no abnormalities | Raise a Work Request for repairs
Control Valve |  | Piston | Diaphragm/ Piston | Exposed to the quality of internal instrument air | To convert air pressure into linear or rotary motion. | Loss of ability to transmit force or respond to control pressure | Piston scoring | •Mechanical wear •Contamination | Dirty air, lack of lubrication, abrasive particles | Air bypass, reduced thrust, unstable motion | Detected via erratic performance | [5 empty] | 0 | Review valve stroke signature online or perform full stroke test | Valve stroke is smooth and consistent with no abnormalities | Raise a Work Request for repairs
Control Valve |  | Piston | Diaphragm/ Piston | Exposed to the quality of internal instrument air | To convert air pressure into linear or rotary motion. | Loss of ability to transmit force or respond to control pressure | Binding or sticking | •Friction from distortion •Internal damage | Thermal distortion, corrosion, or dry contact | Delayed or failed actuation | Detectable | [5 empty] | 0 | Review valve stroke signature online or perform full stroke test | Valve stroke is smooth and consistent with no abnormalities | Raise a Work Request for repairs
Control Valve |  |  | Spring - Actuator | Exposed to the quality of internal instrument air | To return the actuator to a safe position upon loss of air pressure. | Loss of force needed for safe valve positioning. | Fracture or breakage (0 psi output) | •Fatigue •Stress corrosion cracking | Repeated cycling, corrosion, material defect | Valve fails to return to safe (fail) position | Detectable | [5 empty] | 0 | During valve overhaul, inspect actuator spring for cracks, corrosion, or signs of fatigue; replace spring if any defects or loss of integrity are found | Spring intact, free from cracks, corrosion, or deformation; maintains proper preload and elasticity.
Control Valve |  |  | Spring - Actuator | Exposed to the quality of internal instrument air | To return the actuator to a safe position upon loss of air pressure. | Loss of force needed for safe valve positioning. | Corrosion | •Surface pitting | Moisture, salt, contaminated air | Reduced strength, delayed return, eventual fracture | Hidden | [5 empty] | 0 | During valve overhaul, inspect actuator spring for cracks, corrosion, or signs of fatigue; replace spring if any defects or loss of integrity are found | Spring intact, free from cracks, corrosion, or deformation; maintains proper preload and elasticity.
Control Valve |  |  | Spring - Actuator | Exposed to the quality of internal instrument air | To return the actuator to a safe position upon loss of air pressure. | Loss of force needed for safe valve positioning. | Loss of preload | •Bolt loosening •Spring settling | Vibration, improper installation | Inconsistent valve return or slow closure | Detectable | [5 empty] | 0 | Perform full stroke test to detect abnormal stroke behavior | Spring maintains correct preload with bolts secure and properly torqued | Raise a Work Request for repairs
Control Valve |  |  | Spring - Actuator | Exposed to the quality of internal instrument air | To return the actuator to a safe position upon loss of air pressure. | Loss of force needed for safe valve positioning. | Misalignment or seating issue | •Uneven load •Spring buckling | Improper installation, wear on spring guide | Lateral force on stem, sticking, jamming | Hidden | [5 empty] | 0 | Perform full stroke test to detect abnormal stroke behavior | Spring seated evenly with no signs of misalignment, tilting, or buckling; load distributed uniformly. | Raise a Work Request for repairs
Control Valve |  |  | I/P Converter | Exposed to the quality of internal instrument air & environment | To convert an electrical signal into a pneumatic pressure signal. | Failure to convert electrical signal into pnuematic signal | No pneumatic output | •Electrical failure •Internal blockage | Power loss, wire break, nozzle clogging | Actuator receives no signal, valve fails to move | Detectable | [5 empty] | 0 | Perform valve calibration or perform function test the I/P converter to verify electrical input and pneumatic output | I/P converter provides correct and stable pneumatic output in response to electrical signal; no blockage or signal loss. | Raise a Work Request for repairs
Control Valve |  |  | I/P Converter | Exposed to the quality of internal instrument air & environment | To convert an electrical signal into a pneumatic pressure signal. | Failure to convert electrical signal into pnuematic signal | Incorrect output pressure | •Calibration drift •Air leak | Aging, physical damage, contamination | Valve position does not match control signal | Detectable | [5 empty] | 0 | Perform valve calibration or perform function test the I/P converter to verify electrical input and pneumatic output | I/P converter provides correct and stable pneumatic output in response to electrical signal; no blockage or signal loss. | Raise a Work Request for repairs
Control Valve |  |  | I/P Converter | Exposed to the quality of internal instrument air & environment | To convert an electrical signal into a pneumatic pressure signal. | Failure to convert electrical signal into pnuematic signal | Internal corrosion or clogging | •Contaminated air •Moisture ingress | Poor air filtration, coastal exposure | Gradual failure or erratic pressure output | Hidden | [5 empty] | 0 | Perform valve calibration or perform function test the I/P converter to verify electrical input and pneumatic output | I/P converter provides correct and stable pneumatic output in response to electrical signal; no blockage or signal loss. | Raise a Work Request for repairs
Control Valve |  |  | Feedback Mechanism | Exposed, close to the ocean (<500m) | To position the valve accurately in response to the control signal. | Loss of ability to control or confirm valve position. | Valve position mismatch | •Feedback loop failure •Calibration drift | Feedback arm wear, sensor error, electrical noise | Valve position does not match control signal | Detectable | [5 empty] | 0 | Review valve signature or verify valve position feedback against actual valve travel | Valve position feedback matches actual valve position accurately; no drift, error, or loop malfunction | Raise a Work Request for repairs
Control Valve |  |  | Controller | Exposed, close to the ocean (<500m) | To position the valve accurately in response to the control signal. | Loss of ability to control or confirm valve position. | Electronic board failure (smart positioners) | •Component fault •Burnout | Power surge, moisture ingress, aging | No response, incorrect diagnostics, total failure | Detectable | [5 empty] | 0 | Monitor controller diagnostics and alarms for hardware faults | Controller operating normally with no hardware faults, error codes, or abnormal behavior; all input/output functions stable and reliable | Raise a Work Request for repairs
Control Valve |  |  | Solenoid | Exposed to the quality of internal instrument air & environment | To enable or block air supply to the actuator based on an electrical signal. | Failure to switch air flow in response to the control signal. | Fails to energize/de-energize | •Coil burnout •Signal loss •Mechanical binding •Loose/ broken wiring | power failure, loose connection, corossion, poor installation | may fail to fail-safe, no actuation | Detectable |  | Safety |  |  |  | 0 | Function test solenoid by cycling it and verifying response | Solenoid energizes and de-energizes reliably with proper signal; coil intact, wiring secure, and no mechanical sticking. | Raise a Work Request for repairs
Control Valve |  |  | Solenoid | Exposed to the quality of internal instrument air & environment | To enable or block air supply to the actuator based on an electrical signal. | Failure to switch air flow in response to the control signal. | Air leakage (connectors) | •Seal degradation •Seat degradation | Wear, aging, internal contamination | Pressure drop, slow actuator movement | Detectable | [5 empty] | 0 | Inspect solenoid area for drips/stains, audible leak, abnormal pressure drops | All air connectors leak-free with seals intact and properly seated | Raise a Work Request for repairs
Control Valve |  |  | Air Regulator | Exposed to the quality of internal instrument air & environment | To maintain a stable, reduced air pressure to downstream pneumatic components. | Inability to regulate or maintain correct output pressure. | •Pressure fluctuation •No flow | •Mechanical failure •Leakage •Clogging | Damage, corrosion, wear | erratic pressure output, no flow | Detectable | [5 empty] | 0 | Verify air regulator performance by checking pressure gauge readings for stability and expected output | Pressure readings stable and within specified range | Raise a Work Request for repairs
Note on O1: Jakob Verhoef: See Scoring Tab
Note on P1: Jakob Verhoef: See Scoring Tab
Note on Q1: Jakob Verhoef: See Scoring Tab

## Task Header
Equipment Number / FLOC | Task List ID | TL Description | System Condition
1100A0011 |  | Biogo Dosing Service
1100A0011 |  | ATU Pump Out Clean
1100A0012 |  | ATU Pump Out Clean
1100A0012 |  | Biogo Dosing Service
1100A0015 |  | Sewerage System Service
1100A0015 |  | Sewerage System Service
1100A0019 |  | Pump Sewerage Service
1100A0020 |  | Level Tx Calibrate
1100A0027 |  | Sewerage System Service
1100A0027 |  | Sewerage System Service
1100A0029 |  | Biogo Dosing Service
1100A0030 |  | Sewage Clean
1100A0030 |  | Biogo Dosing Service Ops
1100A0032 |  | Sewerage System Service
1100A0032 |  | Biogo Dosing Service Admin
1100A0032 |  | Sewerage System Service
1100A0037 |  | Biogo Dosing Service Chems Eats
1100A0041 |  | Pump Sewerage Service
1100A0043 |  | Sewerage System Service
1100A0043 |  | Sewerage System Service
1100A0044 |  | Sewerage System Service
1100A0044 |  | Sewerage System Service
1100A0045 |  | Sewerage System Service
1100A0045 |  | Sewerage System Service
1100A0048 |  | Sewerage System Service
1100A0048 |  | Sewerage System Service
1100A0049 |  | Sewerage System Service
1100A0049 |  | Sewerage System Service
1100A0060 |  | Whipper Snipping Clean
1100A0113 |  | Bridge Inspect
1100B0003 |  | Cleaning Contractor Audit
1100B0003 |  | Test and Tag
1100CU0002 |  | Radio System Maintenance
1100CU0002 |  | Radio System Service
1100CU0031 |  | Radio Portable EEHA Inspect
1100CU0070 |  | Radio Portable EEHA Inspect
1100CU0071 |  | Radio Portable EEHA Inspect
1100CU0072 |  | Radio Portable EEHA Inspect
1100CU0073 |  | Radio Portable EEHA Inspect
1100CU0076 |  | Radio Portable EEHA Inspect
1100CU0077 |  | Radio Portable EEHA Inspect
1100CU0080 |  | Radio Portable EEHA Inspect
1100CU0081 |  | Radio Portable EEHA Inspect
1100CU0082 |  | Radio Portable EEHA Inspect
1100CU0083 |  | Radio Portable EEHA Inspect
1100CU0084 |  | Radio Portable EEHA Inspect
1100CU0111 |  | Radio Portable EEHA Inspect
1100CU0113 |  | Radio Portable EEHA Inspect
1100CU0116 |  | Radio Portable EEHA Inspect
1100CU0117 |  | Radio Portable EEHA Inspect
1100CU0118 |  | Radio Portable EEHA Inspect
1100CU0123 |  | Radio Portable EEHA Inspect
1100CU0125 |  | Radio Portable EEHA Inspect
1100CU0126 |  | Radio Portable EEHA Inspect
1100CU0127 |  | Radio Portable EEHA Inspect
1100CU0128 |  | Radio Portable EEHA Inspect
1100CU0129 |  | Radio Portable EEHA Inspect
1100CU0130 |  | Radio Portable EEHA Inspect
1100CU0131 |  | Radio Portable EEHA Inspect
1100CU0133 |  | Radio Portable EEHA Inspect
1100CU0135 |  | Radio Portable EEHA Inspect
1100CU0138 |  | Radio Portable EEHA Inspect
1100CU0139 |  | Radio Portable EEHA Inspect
1100CU0140 |  | Radio Portable EEHA Inspect
1100CU0141 |  | Radio Portable EEHA Inspect
1100CU0160 |  | Radio Portable EEHA Inspect
1100CU0162 |  | Radio Portable EEHA Inspect
1100CU0163 |  | Radio Portable EEHA Inspect
1100CU0200 |  | Inspect EEHA
1100CU0202 |  | Inspect EEHA
1100CU0204 |  | Inspect EEHA
1100CU0205 |  | Inspect EEHA
1100CU0206 |  | Inspect EEHA
1100CU0220 |  | Inspect EEHA
1100CU0221 |  | Inspect EEHA
1100CU0227 |  | Inspect EEHA
1100CU0228 |  | Inspect EEHA
1100CU0229 |  | Inspect EEHA
1100CU0230 |  | Inspect EEHA
1100CU0231 |  | Inspect EEHA
1100CU0232 |  | Inspect EEHA
1100CU0238 |  | Inspect EEHA
1100CU0239 |  | Inspect EEHA
1100CU0251 |  | Inspect EEHA
1100CU0327 |  | Inspect EEHA
1100CU0328 |  | Inspect EEHA
1100CU0329 |  | Inspect EEHA
1100CU0330 |  | Inspect EEHA
1100CU0331 |  | Inspect EEHA
1100CU0332 |  | Inspect EEHA
1100CU0333 |  | Inspect EEHA
1100CU0334 |  | Inspect EEHA
1100CU0335 |  | Inspect EEHA
1100CU0336 |  | Inspect EEHA
1100CU0337 |  | Inspect EEHA
1100CU0338 |  | Inspect EEHA
1100CU0339 |  | Inspect EEHA
1100CU0340 |  | Inspect EEHA
1100CU0341 |  | Inspect EEHA
1100CU0342 |  | Inspect EEHA
1100CU0343 |  | Inspect EEHA
1100CU0344 |  | Inspect EEHA
1100CU0345 |  | Inspect EEHA
1100CU0346 |  | Inspect EEHA
1100CU0347 |  | Inspect EEHA
1100CU0348 |  | Inspect EEHA
1100CU0349 |  | Inspect EEHA
1100CU0350 |  | Inspect EEHA
1100CU0351 |  | Inspect EEHA
1100CU0352 |  | Inspect EEHA
1100CU0353 |  | Inspect EEHA
1100CU0354 |  | Inspect EEHA
1100CU0501 |  | Inspect EEHA
1100CU0502 |  | Inspect EEHA
1100CU0503 |  | Inspect EEHA
1100CU0504 |  | Inspect EEHA
1100CU0505 |  | Inspect EEHA
1100CU0511 |  | Inspect EEHA
1100CU0512 |  | Inspect EEHA
1100CU0518 |  | Inspect EEHA
1100CU0519 |  | Inspect EEHA
1100CU0520 |  | Inspect EEHA
1100CU0521 |  | Inspect EEHA
1100CU0530 |  | Inspect EEHA
1100CU0538 |  | Inspect EEHA
1100CU0541 |  | Inspect EEHA
1100CU0547 |  | Inspect EEHA
1100CU0548 |  | Inspect EEHA
1100CU0549 |  | Inspect EEHA
1100CU0550 |  | Inspect EEHA
1100CU0551 |  | Inspect EEHA
1100CU0552 |  | Inspect EEHA
1100CU0553 |  | Inspect EEHA
1100CU0554 |  | Inspect EEHA
1100CU0555 |  | Inspect EEHA
1100CU0600 |  | Inspect EEHA
1100CU0601 |  | Inspect EEHA
1100CU0602 |  | Inspect EEHA
1100CU0603 |  | Inspect EEHA
1100CU0609 |  | Inspect EEHA
1100CU0716 |  | Inspect EEHA
1100CU0717 |  | Inspect EEHA
1100CU0718 |  | Inspect EEHA
1100CU0719 |  | Inspect EEHA
1100CU0720 |  | Inspect EEHA
1100DB0202 |  | Distribution Board Inspect
1100FI0008 |  | Flow Ind Calibrate
1100FI0010 |  | Inst Flow Calibrate
1100FI0012 |  | Flow Tx Certify Calibrate
1100FI0014 |  | Flow Tx Certify Calibrate
1100FIT0161 |  | Inst Flow Verification Flow Tx
1100FIT0165 |  | Inst Flow Calibrate
1100FIT0165 |  | Flow TX Magnetic EEHA Inspect
1100FIT0605 |  | Inst Flow Calibrate
1100FIT0903A |  | Inst Flow Calibrate
1100FIT0903B |  | Inst Flow Calibrate
1100FPP0007 |  | Control Panel Inspect
1100FPP0008 |  | Control Panel Inspect
1100FPP0012 |  | Control Panel Inspect
1100FPP0012 |  | Control Panel Inspect
1100FPP0019 |  | Control Panel Inspect
1100FPP0021 |  | Control Panel Inspect
1100FPP0022 |  | Control Panel Inspect
1100FPP0025 |  | Control Panel Inspect
1100FPP0028 |  | Control Panel Inspect
1100FPP0030 |  | Control Panel Inspect
1100FPP0032 |  | Control Panel Inspect
1100FPP0033 |  | Control Panel Inspect
1100FSS0050 |  | Fire Suppression FM200 Inspect
1100FSS0051 |  | Fire Suppression FM200 Inspect
1100FSS0052 |  | Fire Suppression FM200 Inspect
1100FSS0053 |  | Fire Suppression FM200 Inspect
1100FSS0054 |  | Fire Suppression FM200 Inspect
1100FSS0055 |  | Fire Suppression FM200 Inspect
1100FSS0056 |  | Fire Suppression FM200 Inspect
1100FSS0057 |  | Fire Suppression FM200 Inspect
1100FSS0058 |  | Fire Suppression FM200 Inspect
1100FSS0059 |  | Fire Suppression FM200 Inspect
1100FSS0060 |  | Fire Suppression FM200 Inspect
1100FSS0061 |  | Fire Suppression FM200 Inspect
1100FSS0062 |  | Fire Suppression FM200 Inspect
1100FSS0081 |  | Fire Suppression FM200 Inspect
1100FSS0082 |  | Fire Suppression FM200 Inspect
1100FSS0083 |  | Fire Suppression FM200 Inspect
1100FSS0084 |  | Fire Suppression FM200 Inspect
1100FSS0085 |  | Fire Suppression FM200 Inspect
1100FSS0086 |  | Fire Suppression FM200 Inspect
1100FSS0087 |  | Fire Suppression FM200 Inspect
1100FSS0088 |  | Fire Suppression FM200 Inspect
1100FSS0089 |  | Fire Suppression FM200 Inspect
1100FSS0090 |  | Fire Suppression FM200 Inspect
1100FSS0091 |  | Fire Suppression FM200 Inspect
1100FSS0092 |  | Fire Suppression FM200 Inspect
1100FSS0093 |  | Fire Suppression FM200 Inspect
1100FSS0095 |  | Fire Suppression FM200 Inspect
1100FT0171 |  | Flow Tx Off-site Calibrate
1100FT0181 |  | Flow Tx Off-site Calibrate
1100FT0191 |  | Flow Tx Off-site Calibrate
1100GAC0681 |  | Generator Load Test Service
1100GAC0681 |  | Generator Admin PC Room Test
1100H0001 |  | HVAC Maintenance
1100H0001 |  | HVAC Maintenance
1100H0001 |  | HVAC Maintenance
1100H0208 |  | Joy Sticks Crane #4 Inspect
1100H0413 |  | Drain Pump Lines Clean
1100H0623 |  | Filter Maintenance
1100H0623 |  | Drain Clean
1100IDP0002 |  | Admin PABX Contract Review
1100PIT0601 |  | Pressure Tx Calibrate
1100PIT0602 |  | Inst Press Calibrate Tx
1100PIT0904 |  | Inst Press Calibrate Tx
1100PLC0001 |  | PLC Backup
1100PLC0001 |  | Back Up Battery Test
1100PLC0503 |  | Control System Backup
1100PLC0503 |  | Back Up Battery PLC Replace
1100PLC0504 |  | Back Up Battery PLC Replace
1100PLC0504 |  | Control System Backup
1100PLC0801 |  | PLC Backup
1100PSV0001 |  | PSV Inspect Retest
1100PSV0152 |  | PSV Inspect Retest
1100PSV0162 |  | PSV Inspect Retest
1100PV0601 |  | CV Calibrate
1100PV0602 |  | CV Inspect
1100SB0012 |  | MCC Integrity Test
1100SB0012 |  | MCC Integrity Test
1100SB0012 |  | LV Inspect Thermographic
1100SRN0061 |  | Inspect EEHA
1100SSV0804 |  | Slam Shut Valve Test
1100SUB0001 |  | Substation HV Inspect
1100SUB0001 |  | HV Emergency Lighting Test
1100SUB0001-00EBC0091 |  | Battery Charger Inspect
1100SUB0001-00EBC0091 |  | Battery Charger Inspect
1100SUB0001-00SB0001 |  | Protection Relay Test
1100SUB0001-00TX0001 |  | Transformer Inspect
1100SUB0001-00TX0001 |  | DGA Sample Analysis Tx Test
1100SUB0001-00TX0004 |  | Transformer Inspect
1100SUB0001-00TX0005 |  | Transformer Inspect
1100SUB0001-00TX0007 |  | Transformer Inspect
1100SUB0001-00TX0033 |  | Transformer Inspect
1100SUB0002 |  | Switchroom Emergency Lights Test
1100SUB0002 |  | Substation HV Inspect
1100SUB0002 |  | Sub 2 Integrity Test
1100SUB0002-00EBC0201 |  | Battery Charger Inspect
1100SUB0002-00EBC0201 |  | Battery Charger Inspect
1100SUB0002-00RMU0204 |  | HV Cable Test and Inspect
1100SUB0002-00RMU0204-00TX0015 |  | DGA Sample Analysis Tx Test
1100SUB0002-00RMU0204-00TX0015 |  | Transformer Inspect
1100SUB0002-00RMU0204-00TX0016 |  | Transformer Inspect
1100SUB0002-00RMU0204-00TX0016 |  | DGA Sample Analysis Tx Test
1100SUB0002-00TX0002 |  | Transformer Inspect
1100SUB0002-00TX0002 |  | HV Cable Inspect & Test
1100SUB0002-00TX0006 |  | Transformer Inspect
1100SUB0002-00TX0006 |  | HV Cable Inspect & Test
1100SUB0002-00TX0008 |  | Transformer Inspect
1100SUB0002-00TX0014 |  | Transformer Inspect
1100SUB0002-00TX0014 |  | HV Cable Inspect & Test
1100SUB0003 |  | Substation HV Inspect
1100SUB0003 |  | Room Integrity Test
1100SUB0003 |  | HV Emergency Lighting Test
1100SUB0003-00EBC0301 |  | Battery Charger Inspect
1100SUB0003-00EBC0301 |  | Battery Charger Inspect
1100SUB0003-00EBC0302 |  | Battery Charger Inspect
1100SUB0003-00EBC0302 |  | Battery Charger Inspect
1100SUB0003-00TX0021 |  | Transformer Inspect
1100SUB0003-00TX0025 |  | Transformer Inspect
1100SUB0003-00TX0030 |  | Transformer Inspect
1100SUB0003-00TX0030 |  | TXR HV Cable Inspect
1100SUB0003-00TX0030 |  | Txr TA5 Earthing Inspect
1100SUB0003-00TX0051 |  | Transformer Inspect
1100SUB0003-00TX0051-70T0354 |  | Bund Inspect
1100SUB0003-00TX0053 |  | Transformer Inspect
1100SUB0003-00TX0053-68T0425 |  | Bund Inspect
1100SUB0003-00TX0064 |  | Transformer Inspect
1100SUB0003-00TX0064-68T0426 |  | Bund Inspect
1100SUB0003-00TX0073 |  | Transformer Inspect
1100SUB0003-00TX0073-68T0424 |  | Bund Inspect
1100SUB0005 |  | Compounds MCC Room Integrity Test
1100SUB0005 |  | Compounds HV SR Room Integrity Test
1100SUB0005 |  | Compounds DCS Room Integrity Test
1100SUB0005 |  | Substation HV Inspect
1100SUB0005 |  | HV Emergency Lighting Test
1100SUB0005-00EBC0501 |  | Battery Charger Inspect
1100SUB0005-00EBC0501 |  | Battery Charger Inspect
1100SUB0005-00SB0005 |  | Protection Relay Test
1100SUB0005-00SB0005-00Q0503 |  | 6.6Kv Breakers Service
1100SUB0005-00TX0028 |  | Transformer Inspect
1100SUB0005-00TX0028-25SB0001 |  | Substation Integrity Inspect
1100SUB0005-00TX0028-25SB0001 |  | Inspect Thermographic
1100SUB0005-00TX0029 |  | Transformer Inspect
1100SUB0005-00TX0031 |  | Transformer Inspect
1100SUB0005-00TX0031 |  | HV Cable Inspect & Test
1100SUB0007 |  | Substation HV Inspect
1100SUB0007-00SB0007 |  | HV Contactor Card Replace
1100SUB0007-00SB0007 |  | Protection Relay Test
1100SUB0007-00SB0007-00Q0701 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0702 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0703 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0704 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0705 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0706 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0707 |  | HV Cable Inspect & Test
1100SUB0007-00SB0007-00Q0712 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0713 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0714 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0715 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0716 |  | 6.6kV Switch Service
1100SUB0007-00SB0007-00Q0717 |  | 6.6kV Switch Service
1100SUB0007-00TX0049 |  | Transformer Inspect
1100SUB0007-00TX0050 |  | Transformer Inspect
1100SUB0008 |  | Substation HV Inspect
1100SUB0008 |  | Sub 8 Integrity Test
1100SUB0008 |  | HV Emergency Lighting Test
1100SUB0008 |  | HV Emergency Lighting Test
1100SUB0008 |  | Fire Suppression FM200 Inspect
1100SUB0008-00SB0008 |  | Protection Relay Test
1100SUB0008-00TX0041 |  | Transformer Inspect
1100SUB0008-00TX0042 |  | Transformer Inspect
1100SUB0008-00TX0042 |  | HV Cable Inspect & Test
1100SUB0008-00TX0042 |  | HV Cable Inspect & Test
1100SUB0008-00TX0054 |  | Transformer Inspect
1100SUB0008-00TX0055 |  | Transformer Inspect
1100SUB0008-00TX0055 |  | HV Cable Inspect & Test
1100SUB0008-00TX0056 |  | Transformer Inspect
1100SUB0008-00TX0057 |  | Transformer Inspect
1100SUB0008-00TX0058 |  | Transformer Inspect
1100SUB0008-00TX0059 |  | Transformer Inspect
1100SUB0009 |  | Substation HV Inspect
1100SUB0009 |  | 132KV Sub Integrity Test
1100SUB0009 |  | HV Emergency Lighting Test
1100SUB0009 |  | HV/LV PPE Inspect
1100SUB0009-00EBC0901 |  | Battery/Charger/In INSPECT
1100SUB0009-00EBC0901 |  | Inverter Inspect
1100SUB0009-00EBI0901 |  | Inverter Inspect
1100SUB0009-00SB0009 |  | Protection Relay Test
1100SUB0009-00SB0009-00Q0900 |  | Circuit Break 22kV Maj Service
1100SUB0009-00TX0039 |  | Transformer Inspect
1100SUB0010 |  | AN2 HV Sub 8 Room Integrity Test
1100SUB0010 |  | Substation HV Inspect
1100SUB0010 |  | HV Emergency Lighting Test
1100SUB0010-00EBC1001 |  | Battery Charger Inspect
1100SUB0010-00EBC1001 |  | Battery Charger Inspect
1100SUB0010-00SB0010 |  | Protection Relay Test
1100SUB0010-00SB0010-00Q1002 |  | HV Cable Inspect & Test
1100SUB0010-00SB0010-00Q1007 |  | TRANSDUCER CALIBRATION
1100SUB0010-00TX0045 |  | Transformer Inspect
1100SUB0010-00TX0046 |  | Transformer Inspect
1100SUB0010-00TX0047 |  | Transformer Inspect
1100SUB0010-00TX0047 |  | HV Cable Inspect & Test
1100SUB0010-00TX0048 |  | Transformer Inspect
1100SUB0010-00TX0048 |  | HV Cable Inspect & Test
1100SUB0010-00TX0052 |  | Transformer Inspect
1100SWYD0001 |  | CT 132kV Service
1100SWYD0001 |  | Insulator 132kV Inspect
1100SWYD0001 |  | Surge Arrestor 132kV Service
1100SWYD0001 |  | 132kV Equip Maintenance
1100SWYD0001-00Q0002 |  | Circuit Breaker 132kV Service
1100SWYD0001-00TX0026 |  | Transformer Inspect
1100SWYD0001-00TX0026 |  | Transformer Service
1100SWYD0001-00TX0026 |  | HV Cable Inspect & Test
1100SWYD0001-00TX0026 |  | T/former Isotainer Hydrostatic Test
1100SWYD0001-00TX0027 |  | Transformer Service
1100SWYD0001-00TX0027 |  | Transformer Inspect
1100T0001 |  | Road Drains Maintenance
1100T0175 |  | Drain Inspect
1100T0176 |  | Tank Review External
1100T0176 |  | Tank Ultrasonic Survey
1100T0176-56LIT0403 |  | Inst Level Calibrate
1100T0321 |  | Sump Inspect
1100TIT0603 |  | Inst Temp Calibrate Tx
1100TIT0604 |  | Inst Temp Calibrate Tx
1100TIT0906 |  | Inst Temp Calibrate Tx
1100TV0603A |  | CV Inspect
1100TX0070 |  | Transformer Inspect
1100TX0071 |  | Transformer Inspect
1100UPS0003 |  | UPS Service & Test
1100UPS0004 |  | UPS Service & Test
1100UPS0037 |  | UPS Service & Test
1100UPS0097 |  | UPS Maintenance
1100UPS0099 |  | UPS Maintenance
1100XV0604 |  | Sequence Valve Inspect
1100XV1602 |  | XV Function Test
1100XV1602 |  | XV Overhaul
1100XV1606 |  | Test Function XV
1100XV1606 |  | XV Overhaul
1100Y0004 |  | Pipe Review General
1100Y0005 |  | Valves Lubricate & Exercise
1100Y0009 |  | Pipeline Review External
1100Y0010 |  | Pipeline Ultrasonic Survey
1100Y0010 |  | Pipelines Review External
1100Y0011 |  | Pipe Inspect
1100Y0011 |  | Pipe Inspect
1100Y0012 |  | Valve Inspect
1100Y0060 |  | Pipeline Review External
1100Z0001 |  | Fire Equipment Inspect
1100Z0001 |  | Fire Equipment Inspect
1100Z0001 |  | Fire Equipment Inspect
1100Z0001 |  | Fire Equipment Inspect
1100Z0001 |  | Fire Equipment Inspect
1100Z0001 |  | Fire Equipment Inspect
1100Z0001 |  | Fire Equipment Inspect
1100Z0001 |  | Fire Equipment Inspect
1100Z0001 |  | Fire Equipment Inspect
1100Z0001 |  | Fire System Report Inspect
1100Z0001 |  | Fire Hydrant Flow Test
1100Z0001 |  | Fire Equipment Inspect Ferts
1100Z0001 |  | Fire Equipment Inspect AMM
1100Z0001 |  | Fire Equipment Inspect AN1/2
1100Z0001 |  | Fire Equipment Inspect AN 3
1100Z0001 |  | Fire Equipment Inspect SCP
1100Z0001 |  | Fire Equipment Inspect SMP
1100Z0001 |  | Fire Equipment Inspect AN3
1100Z0001 |  | Fire Equipment Inspect PP2
1100Z0001 |  | Fire Equipment Inspect SMP
1100Z0001 |  | Fire Equipment Inspect Ferts
1100Z0001 |  | Fire Equipment Inspect Ferts
1100Z0001 |  | Fire Equipment Inspect AN1/2
1100Z0001 |  | Fire Equipment Inspect SCP
1100Z0001A |  | Fire Extinguisher Inspect
1100Z0001B |  | Fire Hose Inspect
1100Z12143-00W11155 |  | Manual Valve Inspect
1100Z12143-00W11155 |  | Manual Valve Inspect
1103SB0001 |  | ESD Test
1103T0002 |  | Bund Inspect
1103T0002-03T0015-03T0011 |  | Drain Inspect
1103T0003 |  | Bund Inspect
1103T0004 |  | Bund Inspect
1103T0005 |  | Bund Inspect
1103T0006 |  | Bund Inspect
1103T0007 |  | Bund Inspect
1103T0008 |  | Sump Inspect
1103T0009 |  | Sump Inspect
1103T0010 |  | Sump Inspect
1103T0012 |  | Bund Inspect
1103T0013 |  | Sump Inspect
1103T0014 |  | Sump Inspect
1108B0001 |  | Safety Shower Inspect
1108B0981 |  | Switchroom Clean
1108P0413 |  | Pump Protection Test
1108P0413 |  | Pump Maintenance
1108P0414 |  | Temp Tx Verify
1108P0426-08MP0426 |  | Motor Inspect Major
1108P0427-08MP0427 |  | Motor Inspect Major
1108P0428-08MP0428 |  | Motor Inspect Major
1108P0429-08MP0429 |  | Motor Inspect Major
1108P0430 |  | Flush Pump Clean
1108P0430-08MP0430 |  | Motor Inspect Major
1108P0431-08MP0431 |  | Motor Inspect Major
1108PLC0242 |  | PLC Backup
1108S0515 |  | Filter Review External

## Task Operations
Functional Location / Equipment | Task List ID | Operation Number | Work Centre | Operation Descr | Work | Unit for Work | Special Skills | Qty Resource | Duration | Duration unit | Operation Long Text This is the complete text of the long text, organized by logon language The system will automatically divide the text lines into multiple lines Type: Text Length: unrestricted | Inspectivity Form | Safety Critical | Compliance | Compliance Standard | PMI Doc No
1594Y0010 | 01 | 0010 | XGBS01 | Pipe Inspect Fresh Water Supply |  | HUR | AXGBS | 1 | 2 | HUR | INSPECT FRESH WATER SUPPLY Arrange to have Cooling Tower and Environmental Management Facility make-up valves closed. Record main meter reading at afternoon and following morning to determine any usage. =============================================== JDE MWO: 99005089 JDE Description/Issue: Inspect Fresh Water Supply JDE MWO Requestor Reference: JDE MWO Est Hours: 2 JDE MWO Est Downtime: 0
1594Y15 | 01 | 0010 | XMMF01 | Drain Covers Inspect |  | HUR | AXMMF | 1 | 4 | HUR | Ensure soil buildup is cleaned off drain covers that are subject to accumulation of soil and product build-up Check all drain covers Sign off work order and complete history remarks. =============================================== JDE MWO: 99203103 JDE Description/Issue: Inspect Drain Covers/CHECK DRAIN COVERS JDE MWO Requestor Reference: JDE MWO Est Hours: 4 JDE MWO Est Downtime: 0 |  |  | CO
1594Y15 | 02 | 0010 | XMMF01 | Lined Drains & Pond Inspect |  | HUR | AXMMF | 1 | 0.8 | HUR | JDE MWO: 99202966 JDE Description/Issue: Inspect Lined Drains & Pond/MONITOR LINED DRAINS AND POND JDE MWO Requestor Reference: JDE MWO Est Hours: 0 JDE MWO Est Downtime: 0 |  |  | CO
WESCEF-CSBP-FER-ALB-NPI | 01 | 0010 | XGPL01 | Safety Shower Inspect |  | HUR | AXGPL | 1 | 3 | HUR | JDE MWO: 99005088 JDE Description/Issue: Inspect Safety Shower/INSPECT ALL SAFETY SHOWERS JDE MWO Requestor Reference: JDE MWO Est Hours: 3 JDE MWO Est Downtime: 0 |  | SC
1544B35 | 01 | 0010 | AGSP01 | Stairways Audit (3rd Party) |  | HUR | AXARZ | 1 | 1 | HUR | JDE MWO: 99859785 JDE Description/Issue: Audit (3rd Party)-Stairways/CARBON STEEL STAIRWAYS, WELD FAILURES, CREVICE AND UNDER DEPOSIT CORROSION JDE MWO Requestor Reference: JDE MWO Est Hours: 0 JDE MWO Est Downtime: 0 |  |  |  | Fire
1544B35 | 02 | 0010 | AGSP01 | FRP Audit (Internal) |  | HUR | AXARZ | 1 | 1 | HUR | JDE MWO: 99859782 JDE Description/Issue: Audit (Internal)-FRP/EXPOSURE TO HIGH TEMPERATURE JDE MWO Requestor Reference: JDE MWO Est Hours: 0 JDE MWO Est Downtime: 0
1544B35 | 03 | 0010 | AGSP01 | FRP Audit (Internal) |  | HUR | AXARZ | 1 | 1 | HUR | JDE MWO: 99859781 JDE Description/Issue: Audit (Internal)-FRP/FRP HANDRAILS / MEMBERS, DETERIORATION OF MATERIAL PROPERTY (E.G. BRITTLENESS) JDE MWO Requestor Reference: JDE MWO Est Hours: 0 JDE MWO Est Downtime: 0
1544B35 | 04 | 0010 | AGSP01 | Sheeting Audit (Internal) |  | HUR | AXARZ | 1 | 1 | HUR | JDE MWO: 99859780 JDE Description/Issue: Audit (Internal)-Sheeting/ROOF SHEETING WALL CLADDING, MECHANICAL DAMAGE DUE TO WEATHER, DAMAGED HOLD-DOWN JDE MWO Requestor Reference: JDE MWO Est Hours: 0 JDE MWO Est Downtime: 0
1544B30 | 01 | 0010 | AGOP01 | Building Inspect & Clean |  | HUR | AAGOP | 1 | 6 | HUR | JDE MWO: 99859619 JDE Description/Issue: Inspect & Clean Gutters/CHECK AND CLEAN GUTTERS JDE MWO Requestor Reference: JDE MWO Est Hours: 6 JDE MWO Est Downtime: 0
1544T0339 | 01 | 0010 | XECE01 | Bund Sump Inspect |  | HUR | AXECE | 1 | 2 | HUR | JDE MWO: 99513374 JDE Description/Issue: 5Y Sump Inspection/SUMP INSPECTION JDE MWO Requestor Reference: MCO JDE MWO Est Hours: 2 JDE MWO Est Downtime: 2 | BSD

## FMEA RPN Scoring and Lookup
Scoring
Likelihood
| 1 | Rare | Theoretically possible. Unheard of in a comparable facility. | 1 in 30+ years
| 2 | Unlikely | Has not occurred in the life of the facility but has occurred in the industry. | 1 in 10 years
| 3 | Possible | Has occurred in the life of the facility. Exceptional conditions may allow this event to occur. | 1 in 5 years
| 4 | Likely | Has occurred in the life of the facility and/or a number of near misses have occurred. | 1 per year
| 5 | Almost Certain | Has occurred and repeated events expected in the facility life. Once a year or more frequently. | More than 1 per year
Consequence |  |  | Production Loss (by Plant) | Safety
| 1 | Insignificant | Less than 12 Hours | Minor injury or illness (first aid)
| 2 | Minor | 12 -24Hours | Medical treatment or Restricted Duties injury or illness
| 3 | Moderate | 1-3 Days | Lost Time injury or illness
| 4 | Major | 3-5 Days | Serious permanent disability or death (single)
| 5 | Catastrophic | More than 5 Days | Multiple fatalities
Detectability
| 1 | Almost Certain Detection | Obvious, detection methods reliable e.g. sensors
| 2 | High Probability of Detection | Obvious, detection methods mostly reliable e.g. visual inspection
| 3 | Moderate Probability of Detection | Not obvious, detection methods less realiable not easily inspected visual inspection
| 4 | Low Probability of Detection | Not obvious, specific detection methods required e.g. Non destructive testing
| 5 | Very Low Probability of Detection | Not obvious, advanced detection methods required or dissaembly required e.g. destructive testing
Activity Type
| C1 | Observing Condition - C | Inspection
| C2 | Observing Condition - C | Condition Monitoring
| C3 | Observing Condition - C | Test
| R1 | Repair/Restore - R | Service
| R2 | Repair/Restore - R | Overhaul
| R3 | Repair/Restore - R | Refurbishment
| R4 | Repair/Restore - R | Calibrate
| R5 | Repair/Restore - R | Reset
| R6 | Repair/Restore - R | Repair
| R7 | Repair/Restore - R | Replace
| P1 | Projects / Modify - P | Modification Minor
| P2 | Projects / Modify - P | Capital Project
| P3 | Projects / Modify - P | Major Project
| N1 | Non destructive / Special / Asset Integrity - N | PIS Commissioning Inspection
| N2 | Non destructive / Special / Asset Integrity - N | PIS Thorough Inspection
| N3 | Non destructive / Special / Asset Integrity - N | PIS Review External
| N4 | Non destructive / Special / Asset Integrity - N | PIS NDT Inspection
| N5 | Non destructive / Special / Asset Integrity - N | PIS CUI Inspection
| N6 | Non destructive / Special / Asset Integrity - N | PIS Retest PRD
| G1 | Operational / General - G | Clean
| G2 | Operational / General - G | Operate
| G3 | Operational / General - G | General
Trade
Mech - Fitter
Mech - TA
EI - Electrician
EI - Electrician HV
EI - Instrumentation
Operator
Civil
Plant Inspector
Engineer
Rigger
Time UOM
Hours
Days
Months
Years