Replacement of Pump Mechanical Seal – Cooling Water System

| Doc No | WI-001 |  |  |
| --- | --- | --- | --- |
| Version | 1.2 | Review Date | 01/02/2027 |
| Filename | PMI-P101A-001 |  |  |

| Task | Replacement of Pump Mechanical Seal – Cooling Water System |
| --- | --- |
| Scope / Purpose | To provide a safe, step-by-step procedure for the replacement of the mechanical seal on Pump P-101A. Ensures equipment integrity and prevents process fluid leakage. |
| Asset Status | Operational |

| Safety Notes | Complete appropriate pre-task risk assessment (STOP or JSA). Always assume the equipment is LIVE until positively isolated, locked, tagged and permits issued. PPE Required: Safety glasses, chemical-resistant gloves, steel-capped boots, hearing protection (>85dB area). Hazards: • Residual pressure in pipework – depressurise before breaking any flanges • Chemical exposure from cooling water treatment additives – refer to SDS • Pinch points during seal removal and installation • Manual handling – mechanical seal assembly ~12 kg Controls: • Isolate and lock out pump and associated pipework valves before commencing • Have spill kit available • Use two-person lift for seal cartridge |
| --- | --- |
| Document References | AS 4024 – Safety of Machinery Mechanical Seal – A device that joins the rotating pump shaft to the stationary pump casing, preventing leakage. LOTO – Lockout/Tagout Definitions: SDS – Cooling Water Treatment Chemical Pump OEM Manual: Grundfos CR Series Rev 4 Site LOTO Procedure: LOTO-GEN-001 |
| Notes | Ensure replacement seal kit is on-site before shutdown. Confirm with operations before isolating pump. |

| Instructions | - Where available, record all measurements and results in an Online Inspection Tool (e.g. Inspectivity) or ERP system. - Record Component, Damage and Cause Codes for any issues, defects, or findings in the ERP system. - Capture additional work identified and raise work request in the ERP system. - Record any PMI errors or improvements and raise a master data work request. |
| --- | --- |

Procedure

Prepare

| Step | Instruction | ✓ |
| --- | --- | --- |
| 1 |  | ☐ |

Task Execution

| Step | Instruction | ✓ |
| --- | --- | --- |
| 3 | Disconnect coupling guard (4 x M6 bolts) and set aside. | ☐ |
| 4 | Use coupling puller to remove the flexible coupling insert. Mark orientation before removal. | ☐ |
| 5 | Remove the four pump casing bolts (M12) and carefully withdraw the casing from the seal chamber. | ☐ |
| 6 | Slide the old seal cartridge off the shaft using the seal removal tool. Inspect shaft sleeve for scoring. | ☐ |
| 7 | Clean the seal chamber bore and shaft with lint-free cloth. Apply a thin film of clean water to the shaft for lubrication. | ☐ |
| 8 | Slide the new seal cartridge onto the shaft, ensuring the drive pins align with the shaft slots. Hand-tighten set screws. | ☐ |
| 9 | Reassemble pump casing and torque M12 bolts to 45 Nm in a cross pattern. | ☐ |
| 10 | Reconnect coupling and install guard. Hand-rotate pump shaft to confirm free rotation. | ☐ |

Testing and Return to Service

De-Isolate

| Step | Instruction | ✓ |
| --- | --- | --- |
| 1 |  | ☐ |

|  | Completion | þ Complete |
| --- | --- | --- |
| End | Complete handover of the equipment. - Ensure the work area is left safe and tidy. - Inform Operations or the Control Room the task is complete. - Remove personal locks and tags where applicable. - Complete documentation, logbooks or sign-offs as required by Operations. Comments: | ☐ |
| End | Complete Work Order. - Provide an overall condition rating [1..5] per the scale below in the ERP / Online Inspection Tool - Raise work requests where applicable for any follow-on work. - Record Component, Damage and Cause Codes for any issues, defects or findings in the ERP system. - Return completed documentation to the supervisor. Comments: | ☐ |

| Work Identified |  |  |  |
| --- | --- | --- | --- |
| Task No. | Equip / Component | Work required | Work Request # |

Improvement: How can we improve this document? Is the supplied data correct? Raise a Master Data Work Request and attach marked-up document.

| Rating | Condition Rating | Description | Remaining Life | Typical Action |
| --- | --- | --- | --- | --- |
| 1 | Excellent | Asset in new or as new condition. Very little signs of deterioration. | 100% | No action needed. |
| 2 | Good | Asset still fully functional and performing at required levels. Some deterioration visible. | 75% | No action needed. Keep monitoring. |
| 3 | Fair | Asset still functional but starting to show signs of a reduction in performance. Deterioration visible. | 50% | Will survive to the next shutdown. Start developing a renew / replace strategy. |
| 4 | Poor | Asset still functional but with a reduction in performance. Obvious signs of general deterioration. | 25% | May require work before the next shutdown. |
| 5 | Very Poor | Asset failed or failure imminent. Severe condition dererioration. | 0% | Work required in the next 1-4 weeks. |