Calibration of Pressure Transmitter – Steam Header PT-205

| Doc No | WI-003 |  |  |
| --- | --- | --- | --- |
| Version | 1.0 | Review Date | 10/02/2027 |
| Filename | PMI-PT205-003 |  |  |

| Task | Calibration of Pressure Transmitter – Steam Header PT-205 |
| --- | --- |
| Scope / Purpose | To provide a standardised procedure for the in-situ zero and span calibration of pressure transmitter PT-205. Ensures accurate pressure indication within ±0.1% of full scale. |
| Asset Status | Operational |

| Safety Notes | Complete appropriate pre-task risk assessment (STOP or JSA). Always assume the equipment is LIVE until positively isolated, locked, tagged and permits issued. PPE Required: Safety glasses, heat-resistant gloves, cotton FR coveralls, steel-capped boots. Hazards: • High-pressure steam (1600 kPa, 200°C) in header – severe burn risk • Hot surfaces on pipework and transmitter body • Instrument loop may be tied to automatic control – coordinate with control room before breaking loop Controls: • Confirm steam header is at normal operating pressure before isolating transmitter impulse line • Use heat-resistant gloves when handling transmitter • Place DCS loop in manual before disconnecting signal wiring |
| --- | --- |
| Document References | Rosemount 3051C Reference Manual (Doc 00809-0100-4001) 4–20 mA – Standard analogue signal representing 0–100% of range. Span – The transmitter output at 100% of process range (1600 kPa). Zero – The transmitter output at 0% of the process range (0 kPa). Definitions: AS 60584 – Thermocouples (referenced for temperature compensation) Site Instrument Calibration Standard: INST-CAL-002 |
| Notes | Notify DCS operator before breaking loop. Calibration cert required. |

| Instructions | - Where available, record all measurements and results in an Online Inspection Tool (e.g. Inspectivity) or ERP system. - Record Component, Damage and Cause Codes for any issues, defects, or findings in the ERP system. - Capture additional work identified and raise work request in the ERP system. - Record any PMI errors or improvements and raise a master data work request. |
| --- | --- |

Procedure

Prepare

| Step | Instruction | ✓ |
| --- | --- | --- |
| 1 |  | ☐ |

Task Execution

| Step | Instruction | ✓ |
| --- | --- | --- |
| 2 | With root valve closed and transmitter vented to atmosphere, apply 4 mA signal from calibrator. Trim zero using HART communicator (Sensor Trim > Zero Trim). | ☐ |
| 3 | Connect certified reference pressure source (deadweight tester) to transmitter manifold. Apply 1600 kPa reference pressure. | ☐ |
| 4 | Read mA output on calibrator. Acceptable output: 20.00 mA ± 0.032 mA (0.1% FS). If outside tolerance, perform Upper Sensor Trim via HART communicator. | ☐ |
| 5 | Perform a 5-point linearity check: apply 0%, 25%, 50%, 75%, 100% of span. Record mA output at each point. | ☐ |

Testing and Return to Service

De-Isolate

| Step | Instruction | ✓ |
| --- | --- | --- |
| 1 |  | ☐ |

|  | Completion | þ Complete |
| --- | --- | --- |
| End | Complete handover of the equipment. - Ensure the work area is left safe and tidy. - Inform Operations or the Control Room the task is complete. - Remove personal locks and tags where applicable. - Complete documentation, logbooks or sign-offs as required by Operations. Comments: | ☐ |
| End | Complete Work Order. - Provide an overall condition rating [1..5] per the scale below in the ERP / Online Inspection Tool - Raise work requests where applicable for any follow-on work. - Record Component, Damage and Cause Codes for any issues, defects or findings in the ERP system. - Return completed documentation to the supervisor. Comments: | ☐ |

| Work Identified |  |  |  |
| --- | --- | --- | --- |
| Task No. | Equip / Component | Work required | Work Request # |

Improvement: How can we improve this document? Is the supplied data correct? Raise a Master Data Work Request and attach marked-up document.

| Rating | Condition Rating | Description | Remaining Life | Typical Action |
| --- | --- | --- | --- | --- |
| 1 | Excellent | Asset in new or as new condition. Very little signs of deterioration. | 100% | No action needed. |
| 2 | Good | Asset still fully functional and performing at required levels. Some deterioration visible. | 75% | No action needed. Keep monitoring. |
| 3 | Fair | Asset still functional but starting to show signs of a reduction in performance. Deterioration visible. | 50% | Will survive to the next shutdown. Start developing a renew / replace strategy. |
| 4 | Poor | Asset still functional but with a reduction in performance. Obvious signs of general deterioration. | 25% | May require work before the next shutdown. |
| 5 | Very Poor | Asset failed or failure imminent. Severe condition dererioration. | 0% | Work required in the next 1-4 weeks. |