## WI_Header
Fill in one row per Work Instruction. Set 'Generate?' to YES to include in document run. Fields marked * are required.
Generate? | WI_No * | Document_Title * | Version * | Effective_Date * | Review_Date | Site_Area | Equipment_Asset | Prepared_By | Approved_By | Purpose | References_Definitions | Safety_Risk_Controls | PreStart_Checklist | Isolation_Shutdown_LOTO_Steps | Testing_ReturnToService_Steps | Asset_Tag | Department | Scope | Revision_History | File_Name | Asset_Status | Notes
YES | WI-001 | Replacement of Pump Mechanical Seal – Cooling Water System | 1.2 | 01/02/2026 | 01/02/2027 | Plant A / Cooling Tower Bay | Pump P-101A (Grundfos CR32-5) | James Thornton | Sarah Mitchell | To provide a safe, step-by-step procedure for the replacement of the mechanical seal on Pump P-101A. Ensures equipment integrity and prevents process fluid leakage. | AS 4024 – Safety of Machinery Site LOTO Procedure: LOTO-GEN-001 Pump OEM Manual: Grundfos CR Series Rev 4 SDS – Cooling Water Treatment Chemical Definitions: LOTO – Lockout/Tagout Mechanical Seal – A device that joins the rotating pump shaft to the stationary pump casing, preventing leakage. | PPE Required: Safety glasses, chemical-resistant gloves, steel-capped boots, hearing protection (>85dB area). Hazards: • Residual pressure in pipework – depressurise before breaking any flanges • Chemical exposure from cooling water treatment additives – refer to SDS • Pinch points during seal removal and installation • Manual handling – mechanical seal assembly ~12 kg Controls: • Isolate and lock out pump and associated pipework valves before commencing • Have spill kit available • Use two-person lift for seal cartridge |  |  |  | P-101A | Maintenance | Applies to Pump P-101A only | Rev 1.0 - Initial issue Rev 1.2 - Updated torque values | PMI-P101A-001 | Operational | Ensure replacement seal kit is on-site before shutdown. Confirm with operations before isolating pump.
YES | WI-002 | Inspection and Replacement of Conveyor Drive Belt – Line 3 | 2.0 | 15/01/2026 | 15/01/2027 | Plant B / Production Line 3 | Conveyor C-301 (FlexLink XL Series) | Rachel Nguyen | David Kowalski | To define the procedure for safe inspection and replacement of the drive belt on Conveyor C-301. Minimises unplanned downtime and ensures correct belt tension on return to service. | FlexLink XL Series Maintenance Manual v3.1 Site LOTO Procedure: LOTO-GEN-001 AS 1755 – Conveyors – Safety Requirements Definitions: Drive Belt – V-belt transmitting power from the drive motor to the conveyor head pulley. Tracking – The process of adjusting belt alignment so it runs centrally on the conveyor frame. | PPE Required: Safety glasses, gloves, steel-capped boots. Hazards: • Stored energy in tensioned belt – stand clear during release • Nip points at pulleys and rollers – never reach into moving conveyor • Manual handling – replacement belt weighs 8 kg • Slip/trip hazard from belt debris on floor Controls: • Full LOTO must be applied before any guards are removed • Place belt debris in designated waste bin immediately • Two-person task for belt installation |  |  |  | C-301 | Production | Line 3 conveyor drive belt | Rev 2.0 - Added tracking steps | PMI-C301-002 | Operational | Coordinate with production planner. Allow 2hr for completion.
YES | WI-003 | Calibration of Pressure Transmitter – Steam Header PT-205 | 1.0 | 10/02/2026 | 10/02/2027 | Utilities / Boiler House | Pressure Transmitter PT-205 (Rosemount 3051C) | Tom Vasquez | Sarah Mitchell | To provide a standardised procedure for the in-situ zero and span calibration of pressure transmitter PT-205. Ensures accurate pressure indication within ±0.1% of full scale. | Rosemount 3051C Reference Manual (Doc 00809-0100-4001) Site Instrument Calibration Standard: INST-CAL-002 AS 60584 – Thermocouples (referenced for temperature compensation) Definitions: Zero – The transmitter output at 0% of the process range (0 kPa). Span – The transmitter output at 100% of process range (1600 kPa). 4–20 mA – Standard analogue signal representing 0–100% of range. | PPE Required: Safety glasses, heat-resistant gloves, cotton FR coveralls, steel-capped boots. Hazards: • High-pressure steam (1600 kPa, 200°C) in header – severe burn risk • Hot surfaces on pipework and transmitter body • Instrument loop may be tied to automatic control – coordinate with control room before breaking loop Controls: • Confirm steam header is at normal operating pressure before isolating transmitter impulse line • Use heat-resistant gloves when handling transmitter • Place DCS loop in manual before disconnecting signal wiring |  |  |  | PT-205 | Utilities | Steam header PT-205 | Rev 1.0 - Initial issue | PMI-PT205-003 | Operational | Notify DCS operator before breaking loop. Calibration cert required.
[13 empty] | ☐ Correct replacement seal kit confirmed (Part No. GF-CS32-MK2) ☐ All tools and consumables on-site ☐ LOTO permits issued and signed ☐ Spill kit staged at work location ☐ Area barricaded and signage erected ☐ Permit to Work approved | 1. Notify control room of planned shutdown of P-101A. 2. Stop pump P-101A via local isolator. 3. Close suction valve V-101 and lock with personal lock. 4. Close discharge valve V-102 and lock with personal lock. 5. Attach danger tag to MCC isolator and lock out. 6. Open vent valve V-103 slowly to depressurise casing – confirm zero pressure on PI-101. 7. Open drain valve V-104 to drain casing to drip tray. | 1. Close drain valve V-104 and vent valve V-103. 2. Remove all LOTO devices and tags – confirm all persons are clear. 3. Slowly open suction valve V-101 and check for leaks at seal. 4. Slowly open discharge valve V-102. 5. Start pump P-101A from local isolator and observe for vibration or leaks. 6. Monitor seal faces for leakage for 10 minutes at operating pressure. 7. Confirm flow rate on FI-101 is within normal range (280–320 L/min). 8. Notify control room that P-101A is returned to service. 9. Complete maintenance record in CMMS.
[13 empty] | ☐ Correct replacement belt confirmed (Part No. FL-VB-301, 1520mm x B-section) ☐ Belt tension gauge available ☐ LOTO permits issued ☐ Line 3 production supervisor notified of shutdown ☐ All guards removed and accounted for ☐ Work area clear of personnel | 1. Notify Line 3 supervisor and control room of planned maintenance shutdown. 2. Wait for conveyor to come to a natural stop – do not use e-stop as primary isolation. 3. Isolate conveyor drive motor at MCC DB-3, Lock and tag. 4. Isolate 24V control circuit at Panel CP-301, Lock and tag. 5. Attempt to restart from HMI to prove isolation. 6. Remove drive guard (4 x M8 bolts) and store safely. | 1. Reinstall drive guard and torque bolts to 25 Nm. 2. Remove all LOTO devices – confirm all persons clear of conveyor. 3. Jog conveyor from HMI for 30 seconds and observe belt tracking. 4. Adjust tracking if belt drifts more than 5mm from centre. 5. Run conveyor at full speed for 2 minutes – check for vibration and noise. 6. Verify belt tension with gauge (target deflection: 8mm at mid-span). 7. Notify supervisor and control room that C-301 is returned to service. 8. Update maintenance log in CMMS.
[13 empty] | ☐ Calibration equipment on-site: HART communicator, mA loop calibrator, deadweight tester or reference gauge ☐ Calibration record sheet prepared (Form INST-F-012) ☐ DCS operator notified and loop placed in manual ☐ PTW issued for instrument work on steam system ☐ Hot work area inspected – no ignition sources | 1. Notify DCS operator to place PT-205 loop in manual control. 2. Close impulse line root valve RV-205 to isolate transmitter from live steam. 3. Slowly open vent plug on transmitter manifold to release trapped pressure – confirm pressure gauge reads zero. 4. Disconnect 4–20 mA signal wires at transmitter terminals and connect mA calibrator in series with loop. | 1. Close vent plug on manifold. 2. Reconnect signal wires at transmitter terminals. 3. Slowly open root valve RV-205 to re-pressurise transmitter. 4. Confirm DCS reading matches process pressure on local reference gauge (±0.5% tolerance). 5. Request DCS operator to return loop to automatic. 6. Complete calibration record on Form INST-F-012 and file in calibration database. 7. Affix new calibration label to transmitter with date and technician name.

## Sheet1
1. Close drain valve V-104 and vent valve V-103.
2. Remove all LOTO devices and tags – confirm all persons are clear.
3. Slowly open suction valve V-101 and check for leaks at seal.
4. Slowly open discharge valve V-102.
5. Start pump P-101A from local isolator and observe for vibration or leaks.
6. Monitor seal faces for leakage for 10 minutes at operating pressure.
7. Confirm flow rate on FI-101 is within normal range (280–320 L/min).
8. Notify control room that P-101A is returned to service.
9. Complete maintenance record in CMMS.

## WI_Steps
Work Instruction Database — Procedure Steps
Add one row per step. WI_No must match a value in the WI_Header sheet.
WI_No * | Step_No * | Step_Instruction * | Step_KeyPoints_Hazards | Step_Check | Section
WI-001 | 1 | Gather all required tools and the replacement seal kit (Part No. GF-CS32-MK2). Verify the kit is correct against the pump nameplate. | Incorrect seal kits are a common cause of callbacks. Check OD, shaft size and spring type. | ☐ | Pre-start
WI-001 | 2 | Confirm LOTO is in place and all isolation valves are locked. Check PI-101 reads zero. | Do not proceed if any pressure is present. | ☐ | LOTO
WI-001 | 3 | Disconnect coupling guard (4 x M6 bolts) and set aside. | Tag and bag all fasteners to prevent loss. | ☐ | Task execution
WI-001 | 4 | Use coupling puller to remove the flexible coupling insert. Mark orientation before removal. | Do not use a hammer – this will damage the coupling hubs. | ☐ | Task execution
WI-001 | 5 | Remove the four pump casing bolts (M12) and carefully withdraw the casing from the seal chamber. | Support the casing – do not allow it to hang on the impeller. | ☐ | Task execution
WI-001 | 6 | Slide the old seal cartridge off the shaft using the seal removal tool. Inspect shaft sleeve for scoring. | If shaft sleeve shows scoring >0.2mm, replace sleeve before fitting new seal. | ☐ | Task execution
WI-001 | 7 | Clean the seal chamber bore and shaft with lint-free cloth. Apply a thin film of clean water to the shaft for lubrication. | Do not use oil or grease – this will damage seal elastomers. | ☐ | Task execution
WI-001 | 8 | Slide the new seal cartridge onto the shaft, ensuring the drive pins align with the shaft slots. Hand-tighten set screws. | Push seal squarely onto shaft – do not rock or lever. | ☐ | Task execution
WI-001 | 9 | Reassemble pump casing and torque M12 bolts to 45 Nm in a cross pattern. | Cross-pattern torquing ensures even compression of casing O-ring. | ☐ | Task execution
WI-001 | 10 | Reconnect coupling and install guard. Hand-rotate pump shaft to confirm free rotation. | Binding or stiffness indicates misalignment – do not proceed to start. | ☐ | Task execution
WI-002 | 1 | Confirm LOTO is in place and drive guard has been removed. Inspect old belt for failure mode (cracking, glazing, fraying) and record findings. | Failure mode analysis can indicate misalignment or overload – investigate root cause. | ☐ | Pre-start
WI-002 | 2 | Release belt tension by loosening the motor mounting slide bolts (4 x M10) and sliding motor toward the driven pulley. | Support the motor as you loosen bolts to prevent sudden drop. | ☐ | Task execution
WI-002 | 3 | Remove the old belt from both pulleys and inspect pulley grooves for wear, cracking, or misalignment. | Worn pulley grooves will cause rapid failure of new belt. Replace pulley if groove depth exceeds 2mm. | ☐ | Task execution
WI-002 | 4 | Loop the new belt over the driven pulley first, then the drive pulley. Never use a screwdriver or lever to force belt onto pulley. | Forcing the belt will damage cords inside and cause premature failure. | ☐ | Task execution
WI-002 | 5 | Tension belt by sliding motor away from driven pulley. Use tension gauge: target deflection is 8mm at mid-span under 20N force. | Under-tensioning causes slipping and overheating. Over-tensioning causes bearing failure. | ☐ | Task execution
WI-002 | 6 | Tighten motor slide bolts to 40 Nm. Re-check belt tension after tightening as this can alter position. | ☐ | ☐ | Task execution
WI-002 | 7 | Reinstall drive guard and secure all bolts to 25 Nm. | Confirm guard is fully seated before releasing LOTO. | ☐ | Task execution
WI-003 | 1 | Connect HART communicator to transmitter terminals. Verify transmitter tag and range (0–1600 kPa / 4–20 mA). | Confirm range against calibration record – range may have been changed since last calibration. | ☐ | Pre-start
WI-003 | 2 | With root valve closed and transmitter vented to atmosphere, apply 4 mA signal from calibrator. Trim zero using HART communicator (Sensor Trim > Zero Trim). | Allow 5 minutes warm-up time after connecting calibrator before trimming. | ☐ | Task execution
WI-003 | 3 | Connect certified reference pressure source (deadweight tester) to transmitter manifold. Apply 1600 kPa reference pressure. | Record actual applied pressure from deadweight tester – do not rely on supply regulator gauge alone. | ☐ | Task execution
WI-003 | 4 | Read mA output on calibrator. Acceptable output: 20.00 mA ± 0.032 mA (0.1% FS). If outside tolerance, perform Upper Sensor Trim via HART communicator. | Document as-found and as-left readings on Form INST-F-012. | ☐ | Task execution
WI-003 | 5 | Perform a 5-point linearity check: apply 0%, 25%, 50%, 75%, 100% of span. Record mA output at each point. | All points must be within ±0.1% FS. Fail any point = full recalibration required. | ☐ | Task execution
WI-003 | 6 | Remove reference pressure source. Close manifold vent plug and slowly open root valve RV-205. | Open root valve slowly to avoid pressure shock to transmitter. | ☐ | Testing
WI-003 | 7 | Confirm DCS reading matches local reference gauge within ±0.5% and request operator to return loop to automatic. | Obtain operator sign-off before leaving site. | ☐ | Testing
WI-001 |  | Close drain valve V-104 and vent valve V-103. |  |  | Testing
WI-001 |  | Remove all LOTO devices and tags – confirm all persons are clear. |  |  | Testing
WI-001 |  | Slowly open suction valve V-101 and check for leaks at seal. |  |  | Testing
WI-001 |  | Slowly open discharge valve V-102. |  |  | Testing
WI-001 |  | Start pump P-101A from local isolator and observe for vibration or leaks. |  |  | Testing
WI-001 |  | Monitor seal faces for leakage for 10 minutes at operating pressure. |  |  | Testing
WI-001 |  | Confirm flow rate on FI-101 is within normal range (280–320 L/min). |  |  | Testing
WI-001 |  | Notify control room that P-101A is returned to service. |  |  | Testing
WI-001 |  | Complete maintenance record in CMMS. |  |  | Testing

## Instructions
Field Descriptions & Instructions
HEADER FIELDS
WI_No | Unique identifier for the work instruction, e.g. WI-001
Document_Title | Full title of the work instruction document
Version | Document version number, e.g. 1.0, 2.1
Effective_Date | Date the document becomes active (DD/MM/YYYY)
Review_Date | Scheduled date for next review (DD/MM/YYYY)
Site_Area | Physical site or area where the work instruction applies
Equipment_Asset | Name or ID of the equipment or asset covered
Prepared_By | Name of the person who authored the document
Approved_By | Name of the authorising person
Purpose | Brief statement of what this work instruction covers and why
References_Definitions | Any standards, procedures, or terms referenced
Safety_Risk_Controls | PPE requirements, hazards, risk controls, and safety notes
PreStart_Checklist | Items to verify before starting the task
Isolation_Shutdown_LOTO_Steps | Lock-out/tag-out and isolation steps as free text
Testing_ReturnToService_Steps | Steps to test and return equipment to service
STEP FIELDS
WI_No | Must match a WI_No from the WI_Header sheet
Step_No | Sequential step number, e.g. 1, 2, 3 (or 7.3.1, 7.3.2)
Step_Instruction | Full instruction text for this step
Step_KeyPoints_Hazards | Key points, warnings, or hazards specific to this step
Step_Check | Checkbox label or pass/fail criterion for this step
Section | Which procedure section this step belongs to: Pre-start / LOTO / Task / Testing